## Sheet1
Ministry of Energy and Water Resources
Somali Electricity Recovery Project
Project Implementation Unit (PIU)
PRE-BID CONFERENCE
HEALTH FACILITIES - SOUTHWEST STATE - 25 APRIL 2024
ITEM NO. | BID REFERENCE | ITEM DESCRIPTIONS | RESPONSE FROM PIU/MINISTRY
1 | Deadline for submission of bid(ITB 23.1) | We kindly request an extension of minimum three (3) weeks.Due to the extensive scope of these exciting tenders, as well as the Ramadan/Eid public holidays where activities have been put on hold, combined with long courier times for international submission of bids, this will give the bidders the sufficient time to submit their most competitive proposal, ensuring best value to the employer. | The project is behind schedule and due to that the Ministry can no longer extend the submission deadline. Therefore all bidders are encourage to submit their bids as per the submission deadlines stipulated in the bid document. No further extension granted.
2 | Form of submission (ITB 22.1) | Considering the delivery challenges and extended delivery times experienced with courier services like DHL Express and TNT, could we explore the possibility of submitting bids electronically to ensure efficiency and timeliness? | No electronic submissions are accepted. The Ministry shall not take the responsibility of any bids submitted through courier services such as DHL. Only bids submitted physically to the Ministry's offices shall be considered for evaluations.
3 | Financial Bid Opening (ITB 26.6) | Given that electronic bid submission is not permitted and financial envelopes are not password-protected, how will the security of financial bids be handled, preventing any premature opening. In the interest of transparency and adhering to best practices, we kindly request that the total bid amount for all submissions be disclosed during the public bid opening. Thanks for your kind consideration in this regard. | The bid is based on the two envelope bidding process which doesn't allow any opening of the financial envelopes during the 1st bid opening stage where only technical bid shall be opened. The security provided is that all financial bids shall be isolated during the 1st opening, put in separate container/box,sealed off, signed and initialled by all the bidders' attendees. When the financial bids for the contractors who proceeded to the second round (financial stages )are to be opened, all the initial provisioned security measured shall be considered and checked. After all, financial bid opening shall occur in the presence of the contractors who have succeedeed to proceed to next stage which is the financial bid. Separate USB for the Technical Bids and the Financial Bid and included in their separate envelopes.
4 | Scope of Works for the Security Personal (RFB Section 3.5.1) | The tender states “In addition to the above technical personnel, contractor shall also hire security personnel to guard and protect the facility round the clock. Minimum 2 people is recommended for the day and night shifts.” Please confirm that once the contractor has installed/commissioned the sites, the physical security of the assets will be the responsibility of the end-users, and at the same time kindly clarify the role and quantity of the security team. | During O&M stage, the security of the facility shall remain in the hands of the contractor. The security personnel are meant for day/night shifts and the bare minimum is to ensure the facilities are guarded throughout during the O&M period.
5 | In section 2.3.1.2.2, | the Performance Warranty specifies that PV modules should not experience degradation in power generation exceeding 0.5% per annum and guarantee a performance level of 90% after 25 years of service. However, in section 2.3.13 of the GTP, it is stated that the performance level is 90% up to 15 years and 88% up to 25 years. This requires clarification. | GTP details prevail
6 | In section 2.3.5, | the Battery Energy Storage System (BESS) specification states that the battery should have a life cycle of more than 5000 cycles at 95% Depth of Discharge (DOD). However, in section 2.3.13 of the GTP, it is mentioned that the cycle life is 5000 cycles to 80% capacity at 25 degrees Celsius. This requires clarification. | GTP requirement prevails
7 | ITB 11.1 (j) | In Section IV - Bidding Forms - ES Management Strategies and Implementation Plans (ES-MSIP) there is a reference to ITB 11.1 (j) of the Bid Data Sheet. - This section does not exist. | Refer to 11.2 (i)
8 | 2.3.13 GUARANTEED TECHNICAL PARTICULARS | The Bidder must submit duly filled Guaranteed Technical Particulars (GTP) for each major equipment; duly completed and signed by the Manufacturer of the equipment and submi􀆩ed together with relevant copies of the Manufacturer’s Technical data sheet, catalogues, brochures, drawings, technical data & calculations, documentary evidence indicating manufacturer’s supplies record, details of manufacturing capacity, the manufacturer’s experience, copies of complete type test reports and accredita􀆟on cer􀆟ficate for the testing laboratory for tender evaluation, all in English language. It is asking the GTP to be filled in and signed by the Manufacturer but at the end of the GTP form, it requires the Name of the Bidder and Signature of the Bidder? | Please refer to 11.2 (i)-( j)- it is either
9 | N/A | Certain Facilities, notably hospitals have a grid connection and backup DG sets in certain cases. Grid supply at these facilities is available for approx 24 hrs/day. Our understanding is that solar systems to be supplied are OFF GRID. Pls confirm that no connecivity is required to the electrical grid or to the backup DG Generators? | Solar PV and BESS are supposed to be the primary source of power for these facilities. Grid Connection and that of DG shall serve as back up. The proposed system shall take into account the integration of these various system. Hence Hybrid mechanism required shall support multiple source of power
10 | N/A | At locations where nonfunctional solar installations are installed. Are we authorized to remove and replace these systems? | No. since the existing solar fcailities are outside of this current project scope
11 | N/A | At locations where the target capacity cannot be installed due to insufficient exposed area or roof space, the installed capacity can be reduced. (Laansalati General Hospital for example) | Stick to the requirement. The designed minimum capacity shall be achieved.
12 | N/A | The availability of electricity from the grid at the general hospital facilities is good. We propose and seek your concurrence to supply hybrid rather than OFF-GRID PV systems at these 4 locations | The system is hybrid capable of integrating multiple source of power
13 | N/A | The tender document requires the installation of single phase (240V AC) power supply for installation of 30kW or less. If some maternity hospitals or health centers are wired for 3 phase supply, we seek your concurrence to install 3 phase PV systems at these locations. | Both single and three phase inverters are allowed provided that the electrical infrastructure i.e. Switch boards and cabling can support the proposed inverter voltage configuarion
14 | N/A | Each of the 4 general hospital facilies included in the RFB # SO-MOEWR-398960-CW-RFB are connected to the electrical grid with regular access to electrical grid power. As such, energy generated from the planned Off-grid hybrid solar power plant would either be used to replace the existing grid power supply or to replace it during periods of power outages. | For facilities with an existing Utility connectivity and that of DG, Off Grid shall not be proposed. Recall the title of the tender reads'' Design, Supply, Installations, Testing and commissioning of Hybrid/Off-Grid Solar PV…..'' meaning the facilities where there are existing utility connectivity and back up DG, the proposed system shall be of Hybrid capable of accepting power from multiple sources.
15 | N/A | We seek your concurrence to propose to MOEWR, either a guarantee backed leasing arrangement of grid connected solar equipment installed at each of the 4 hospital facilies or an energy sale/purchase arrangement of generated power by the solar plant supplier. Either arrangement offers improved sustainability of electricity supply to the general hospital facilies and liberates financial resources within MOEWR to invest in Off-grid solar hybrid installaons at non electrified health facilies. Best Regards | Kindly stick to the requirement in the bid. Leasing isn't permitted.
16 | Mounting structure requirements | Please state if there are any preferences by the end-users regarding the mounting of the PV panels (roof mounted/ground mounted) for the different sites. The consideration can also be made based on the structural strength of the building rooftop. | No preference but depends on site conditions. Successful contractor shall do due dilligence in finding out what is best for the site.
16 | Building plans | Please share any structural drawings of the buildings, especially the general hospitals. | Some of these building have been built decades ago, no structural drawings are available. It is therefore highly recommended for bidders to arrange voluntary random site visits to appraise themselves with the reality on the ground.
17 | Containerized solution | Please confirm if containerized solution incorporating the hybrid inverters and the batteries can be offered for the general hospitals. | Allowed as per specifications
18 | N/A | Alternately, please confirm if there is adequate space inside the hospital to install the required inverters, batteries and electrical distribution and protection systems. | Spaces are available. However, it is contractor's obligation to make ground related due dilligence and confirmation on what works for their proposed systems
19 | Technical rooms | Please confirm if there is adequate space within the maternity hospital and health center building premises to install the required hybrid inverters, batteries and electrical distribution and protection systems. | Spaces are available. However, it is contractor's obligation to make ground related due dilligence and confirmation on what works for their proposed systems
20 |  | Alternately, please confirm if we can offer to build a small technical room (3metersx2.4metersx2.5meters) outside the health centers or maternity hospital building to house all the electrical equipment for the PV systems. | Spaces are available. However, it is contractor's obligation to make ground related due dilligence and confirmation on what works for their proposed systems
21 | Location of existing main distribution boards | Please provide the location of the existing main distribution boards (or distance from container to MDB) so the cables connecting the new distribution board to the existing distribution board can be sized and routed. | Most facilities don't have unified standarized main /sub main distribution systems. Mostly don't have properly manufactured/fabricated switchboards with the required protection. It is this sole reason that in this current bid scope, there is provision for all these mishaps to be addressed and standarized to offer the required switching/isolation and protection. Therefore, bidders are highly urged to make voluntary site visits to some random sites to appraise and make understanding on the ground situations which shall inform on their costing strategy.
22 | Presence of diesel generator on site | Please clarify if there are diesel generator on site(s). If yes, then please clarify on the following: 1. Make, model, rated output power of the diesel generator (please share datasheet if possible) | Some facilities got Generators, others don't. Sizes differ as well. Depending on facilities, sizes range from 70kVA to 350kVA mostly for referral hospitals. Smaller Maternity and Health facilities, majority don't have any Generator back up sets. Models differ, what is common are cummins are perkins.
23 | N/A | Please confirm if the proposed inverters (for all 3 types of buildings, are required to turn on/off the diesel generator in case of unavailability of PV power) | Priority shall be for ESS first then after ESS is about to deplete then inverter shall trigger an external Auto-change over to switch on the Generator Set.
24 | AC-Coupled system | Are DC-Coupled solution acceptable as they are more cost and energy efficient than AC-coupled solution, and DC-coupled solutions involve fewer energy transition stages | Both options are allowed either DC-AC or DC-DC coupling
25 | Wind speed requirement | Please clarify if there are explicit wind speed requirements for the PV mounting structures. Alternately, please confirm if a maximum wind speed load of 100 Km/hr can be considered based on the local wind conditions. | It is allowed provided that the panels and associated structures shall withstand the required wind load
26 | Container Location | The bid requires a containerized solution as per the below statement found on page 160. Can you please specify the location of the container in each site. Control room containerized solution for all indoor equipment including BESS, Inverters, Air Conditioning, IT devices etc. | Containerized solutions are required. Locations shall be proposed by the successful bidder and submit as part of the shop drawings for approval/
27 | Internal rewiring | As the scope of “internal rewiring” is vague, and as there are 30 sites, we appreciate if this can be quoted separately (as OPTIONAL) to avoid its effect on the evaluation of the bid. Alternatively, kindly specify the number of rooms in each facility so that we can estimate the amount of “internal wiring” works requested | Kindly quote as per the bid. For the Number of rooms, bidders are urged to make their own local arrangement to familiarize themselves with the ground situation.
28 | Site Locations | Kindly provide the coordinates for the 30 sites. | This data is not available
29 | Containeraized Solution Description | Kindly confirm that the containerized solution mentioned in the tender refers to the one of the ISO containers as per below: | These shall be the purpose made type containerized solutions by the manufcaturers not this dry type shown below. Shall have all associated services such as cooling and ventilation systems. It is factory built type from manufacturers
30 |  | The Bidders are required to attach Award letters and completion certificates for the previous and current projects. We require clarification if both the award letters and completion certificates are required for each project or if either will suffice. | Submission of both the award letters and the completion certificates are required. For the ongoing contracts, award letters suffices.
31 |  | Audited Accounts are required for the past five years from the year 2019 to 2023, in some countries the Audit of year 2023 accounts has not been concluded. In such case the should the Bidder attach the Audited accounts for years 2018 to 2022. | Bidders in countries whose the year 2023Auidt has not been concluded, shall provide additional evidence to reinforce their assertion. Only then, will the Ministry accept Audited Accounts of 2018-2022 is acceptable.
32 |  | The bidders are required to provide profiles of specialist subcontractors for Civil and Mechanical works. In case the bidding contractor has capacity and experience to undertake such works in-house, do they need to include the profiles of subcontractors? | They don't need to include as long as they can show as part of their documentations that the company have adequate capacity to undertake the specialist works
33 |  | In the technical evaluation criteria, the detailed design has been allocated 12 marks. Clarify if provision of detailed designs is a mandatory requirement? | It is mandatory and shall be included as part of the mandatory requirement under item 11.2 (i)-(m)
34 |  | Bidders are required to provide Statutory documents (registration and certification documents), Should the documents be certified by a commissioner of oaths? | Registration and certification documents of eligible countries of Bank financed operations are acceptable.
35 | Technical score pass mark | In technical evaluation, the pass mark for technical evaluation is not provided in the RFB document, we request clarification on the pass mark for the technical evaluation. | Please refer to ITB 32.2. The technical pass score is 70% as indicated in the bidding document.
36 | Operations and Maintenance (O&M) Costs | How does the O&M cost be factored in after the initial 2 years O&M Services. | The quoted price for the O&M services shall remain the same throughout if the contract for the services needs to be extended beyond the currently estimated 2 years.
37 | Contractors associations | How is the JV Partnership is being evaluated with regard to their roles | Bidders shall refer to the pages of 58-68 under section III about Evaluation and qualification criteria
38 | N/A | Is it allowed certain facilities to be quoted for instead of the lot in its entirety | Not at all. The lot shall be quoted completely. Sectionalized bidding isn't allowed
39 |  | Is it required to have Tax compliance certificate by bidders | Yes and its Mandatory. Shall be submitted as part of the Mandatory requirement.
40 |  | Under ITB 11.2 (m) of the BDS shall be modified to read as shown on the next column | Detailed design of the proposed system showing all necessary technical assumptions applied, calculations, system sizing, spare capacity, projected system losses etc. The design shall cover the major equipment/devices including Modules, Arrays, Mounting Module Structures, Combiners, Inverters, Battery Inverters, Batteries, Communication & Monitoring system, Switchgears, Protection, Earthing and Lightning Protection, Cables (both DC & AC), HVAC system and any other system required to make the plant functional. Bidders to submit electrical schematic diagram of the proposed PV systems design and configuration showing the main equipment/components and control equipment/switchgear, their interconnection, and the power flows. One diagram for EACH type of facility; General Hospital, Maternity Hospital and Health Centre.