## Sheet2
Ministry of Energy and Water Resources
Somali Electricity Recovery Project
Project Implementation Unit (PIU)
PRE-BID CONFERENCE
RFB NAME: | Design, Supply, Installation, Testing & Commissioning of 4.3MWp Solar PV Power Plant with 9.0 MWhr of BESS including 9km of 33kV Evacuation line for National Electric Power Company (NEPCO), Galkayo, Puntland State, Somalia
RFB No. | SO-MOEWR-459168-CW-RFB
ITEM NO. | BID REFERENCE | ITEM DESCRIPTIONS | CLARIFICATION SOUGHT BY THE BIDDER | RESPONSE FROM THE EMPLOYER
1 |  |  | We kindly request the sharing of land corner coordinates and, if available, soil survey data in order to facilitate the progress of the feasibility and engineering phases. | Refer to the provided coordinates in the bid for land corner coordinates.
Soil survey data- refer to the geotechnical report which shall be shared and posted in the website
2 | Volume I: Bidding Procedure and Contract Forms Bidder Qualification Section III - Evaluation and Qualification Criteria 4.2(b) Specific Experience | (b) For the above or other contracts executed during the period stipulated in 4.2(a) above, a minimum experience in the following key activities: Design, supply, installation, testing and commissioning of megawatt-scale hybrid PV plants 15MWp DC Solar PV 5MW/20MWhr BESS in Africa with associated substation and evacuation systems of a minimum 33kV rated system. | Evaluation and Qualification Criteria of the bid document, specifically for the condition requiring experience with a 15 MWp Solar PV Plant and a 20 MWh BESS. Necsom bid The Bidder proposes allowing under-construction hybrid PV and BESS projects, up to the 33 kV MV system, to be considered as valid references. The Bidder also requests allowing projects from anywhere in the world instead of restricting eligibility to the Africa region. | The requisite experience of the similar projects of 3No. Shall remian as indicated in the bid and should have been completed six( 6) months before the submissionn date of the bid. The whole idea is to get competent contractor with past similar experience.
The required similar completed projects can be referenced to any where in the globe not necessarily in a frica.
3 | Volume I: Bidding Procedure and Contract Forms Commercial PCC 30. Limitation of Liability PCC 30.1 (b) | PCC 30.1 (b) The multiplier of the Contract Price is: 110% | Bidder proposes limiting the LOL to a maximum of 100%, aligning with standard market practices for renewable energy projects. | Employer tried to be fair in terms of apportioning the risks. Looking at the nature of the project, 110% LOL looks reasonable and fair amount. Therefore, the LOL of 110% remains as is in the bid.
4 | RFB Documents General Site Studies | Site studies such as : 1. Geotechnical Study(Including Soil test, Corrosion Test, Borehole test, Pull-out test, ERT, TRT etc.) 2. Hydrology Study 3. Topo Study 4. ESIA Study 5. Grid Assessment report or the Grid Impact Study | Bidder requests the Employer to share the specified site-related studies to facilitate the design of plant facilities, including foundation type, cut-fill quantities, road design, requirements for man-made drains, site-specific environmental issues, and mitigation strategies. These studies will enable us to prepare a comprehensive and optimized proposal tailored to the specific site requirements. | Geotechnical studies ( including the hydrology and Topo ) & ESIA shall be posted in the employer's website. Grid assessment or Grid impact study for distribution network is still on-going.However, there is adequate information in the bid that can allow the bidder to prepare their bid. In terms of Grid integration, their scope ends at the distribution Substation. From there, the utility Service provider will off-take and distribute to the downstream load centers
5 | Volume I: Bidding Procedure and Contract Forms General ITB 23.1 | The deadline for Bid submission is: Date: 10 February 2024. | The Bidder requests an extension of the bid submission deadline to 15th May 2025 for the below reasons. The data requested in above point 4 is not provided in tender document Volume I and II. After PIU office provides this data, our technical teams shall study the documents. They shall visit and study the site. Makes analysis, reports and then prepare the bid. All these activities consume several week time and Hence requested for Bid closing date Extension as requested above. | Employer has given enough time for bidders to work on their bid preparation and submissions. Therefore, the referred submission date in the bid still remains un-changed
6 |  |  | Is there a document with clear land boundaries? | Coordinates have been provided in the bid which clearly shows boundaries of the proposed new site
7 |  |  | How many W minimum is desired to be used as panel power? If there is no limitation, can we plan it? | No limitations on the Wattage of the PV panel. However, for proper use and utilization of the space, the employer recommends the use panels/modules of higher rating subject to the client approval
8 |  |  | It is planned to use 5500 kVA for transformer power, can you confirm this? | Minimum required is 5.5/6.5MVA (ONAN/ONAF) type of transformers. Therefore, use of 5.5MVA (ONAN) is permitted provided all the rest of the specifications in the bid are adhered to.
9 |  |  | Can you confirm that water tank, wire fence, entrance gate, guard shack, CCTV system and lighting system will be provided by the EMPLOYER? | Refer to the Civil & structural works section in the employer's requirement for more clarity on the scope of the builders work. However, take note on the amendments as shown below.
- Water harvesting and storage tanks, plant area lighting shall be provided by the contractor
- Perimmeter fence , perimeter lighting, guard house, office building for the employer's staff, latrines and rest rooms are to be given by the local Electricity Service Provider
- CCTV to be used in securing the projects materials shall be provided by the contractor since site security is solely on the contractor's scope
10 |  |  | Can detail information be given for the administrative building (in m²)? | - This shall be designed in coordination with the contractor at the execution stage
11 |  |  | Will the panel carrier systems be aluminum? | Yes provided it is hot dipped galvanized and in line with the provided specifications in the bid document
11 |  |  | Will the operation, maintenance and repair belong to the CONTRACTOR? | Operational and maintenance of the plant shall be handled by the local Electricity Sevice Provider. However, for repair works - anything arising out of the project related defects then contractor has to undertake in line with the defect liability based on the terms given in the contract. Things to do with the functional guarantee and plant performance, contract clearly stipulates on how to handle it.
|  |  | Will aggregate paving be done all over the site? Or should it be only under the panels? | Overall site preparation and back filling is to be undertaken by the Electricity Service Provider. However for any builders work necessary for the erection of the power plant other than specified in the scope of the ESP shall be handled by the contractor
12 |  |  | How many times a year will panel cleaning be done and whose scope will it be? | Cleaning is part of the preventive maintenance which shall be undertaken by the local Electricity service provider not on the scope of the contractor.
13 |  |  | Is there a document showing the ETL (Energy Transmission Line) route and what is our scope at the connection point? | Yes there are drawings showing the route for the line. Which shall be shared and posted on the website
- In terms of the connection point, the contractor scope ends at the distribution substations after connecting to the 2No. 5/6.5MVA 33/11kV step down Transformers. The rest of the distribution to the downstream load centers is in the scope of the ESP
14 |  |  | Is there an origin requirement for products? Can Chinese products be used? | Yes there is an origin declaration form to be filled for eligibility and compliance grounds. Employer has no preference in terms of products to be used provided the relevant specifications can be adhered to
15 |  |  | Is there a BOQ or similar document? | Refer to the price schedules provided in volume one of the bid document for pricing purposes
16 |  |  | Is there a breakdown table for quotation? | Refer to the price schedules provided in volume one of the bid document for pricing purposes
17 |  |  | Is there a spare material list? | Refer to the price schedules and to the employers requirement
18 |  |  | Proposed area/land for PV (length x width). | Refere to the provided coordinates in the bid
19 |  |  | PV Plant Setting Out Plan (if available) | Employer shall hand over a green field area with basic infrastructures to be done by the ESP. Contractor is suppose to undertake the power plant setting out plan since its the contractor's scope to do both design and the build.
20 |  |  | Any detail RFQ/report available for these SLDs mentioning PV Capacities (kWp), Battery Capacity (kwh), Inverters . | Refer to the SLD enclosed in the bid document
21 |  |  | Timeline for project construction/completion. | Refer to the SPN enclosed in bid document and the proposed PCC of the contract
22 | Regarding the minimum reference projects as stated in the RFB: “b) For the above or other contracts executed during the period stipulated in 4.2(a) above, a minimum experience in the following key activities: | Design, supply, installation, testing and commissioning of megawatt-scale hybrid PV plants 5MWp DC Solar PV, 2MW/9MWhr BESS in sub-Saharan Africa with associated substation and evacuation systems of a minimum 33kV rated system. “ | Can an alternative to that be the cumulative installation of 5 MWp and 9 MWh for several sites? | It's not cumulative. It is separate stand alone 3No. projects of the 5MWp and 9MWHr capacity each
23 | 4.2(a) Specific Experience | (a)Participation as contractor, joint venture member[1], or subcontractor, in at least three (3) contracts within the last ten (10) years, each with a value of at least USD 6,000,000 (United States Dollars six million) that have been successfully and substantially completed | We seek clarification on whether the eligibility criteria can be met by completed solar projects alone, or if the submitted contracts must specifically involve hybrid systems, such as Solar and Battery integration. | The refered amount refer to the hybrid projecs of the combination of the solar PV and BESS
24 |  | Minimum average annual turnover in Solar Energy Sector of USD $12 Million. calculated as total certified payments received for contracts in progress or completed within the last ten (10) years. | We request an amendment to this clause, reducing the requirement to USD 10 million within the last ten years. | 12 Million is the minimum requiste annual turnover required.
25 | 4.2(b) Specific Experience | Design, supply, installation, testing and commissioning of megawatt-scale hybrid PV plants 5MWp DC Solar PV, 2MW/9MWhr BESS in sub-Saharan Africa with associated substation and evacuation systems of a minimum 33kV rated system | Kindly confirm whether the required experience is based on the capacity at a single location or the cumulative capacity across multiple locations. | It's not cumulative. It is separate stand alone 3No. projects of the 5MWp and 9MWHr capacity each
26 |  |  | Please share if available either theTopo survey (in Auto Cad) or the KMZ file of the Site | Refer to the Geotechnical documents in the website
27 |  |  | Kindly elaborate on the 9km 3phase UG line of 3C 185mm2 cable. Does it mean there will be a parallel underground evacuation line to the overhead line? | Yes there is separate underground circuit parallel to the overhead line
28 |  |  | Are we going to have OPGW or AEW on the overhead network? Clarify so that we can factor in materials and cost accordingly. | Either way can work. You can use either OPGW or aerial wire to provide requiste line protection against lightning
29 |  |  | Can the power transmission network be re-routed to an optimized one or current route fixed | The provided route is final
30 |  |  | Is T/L double or single circuit | It is a single circuit for the overhead and one circuit for Underground line
31 |  |  | Need normal earth wire and OPGW for lightning protection or does not need any earth wire. | Refer to the answer of Q.28
32 |  |  | If any telecommunications equipment is required in hybrid PV+BESS | Refer to the SCADA & EMS section of the bid and the requisite network back bone that will enable the system to function proper. All telecom infrastructure necessary for proper function of the remote monitoring and control of the power plant shall be provided by the contractor.
33 |  |  | Is SCADA required for remote 33/11kV or just RTU? | RTU can be used in the distribution substation provided that it is linked up with the master station of SCADA in the main power plant
34 |  |  | Are the provided SLDs intended solely for reference, or are we required to proceed with the same design? | Provided SLDs are suppose to guide the contractor in coming up with its detailed design. It sets the basis for the employer's minimum requirement.
|  |  | Can the proof of cash flow be based on the audited report for the year 2023? Can the 2024 data be omitted? If 2024 data is required, can unaudited financial statements be used? Our financial data for both 2023 and 2024 fully meet the requirements, but the audit for the 2024 financial data has not been completed yet. | On matters of cash flow, the bidder shall demonstrate its access or availability of liquid assests, cash at hand or line of credit facility from the bank as a proof of the cash flow requirement.
For the audite accounts, required audited accounts are from 2016-2023.
|  |  | Is it necessary to provide supporting documents for the minimum average annual turnover, or is it sufficient to fill in the data? The tender document does not explicitly require the submission of supporting documentation. It only mentions the basis for the calculation. | The turn over data shall be generated from audited certified financial statements of the company. Since its an extract, the two shall match and be an accurate reflection of the data provided in the financial statements
|  |  | is the AC capacity of BESS is 2MW or 3MW? | Minimum BESS power rating is 2MW With a minum C rating of 0.25 C