## AAAC 100mm2
Mini Grid Project
Guaranteed Technical Parameters
Conductor: AAAC 100 mm2
Description | Unit | Guaranteed Value
|  | Required | Offered
Name of manufacturer
Country of manufacture
Type |  | AAAC
Standard | IEC | IEC 60189
Conductor material |  | Aluminium Alloy
Conductor code name |  | AAAC
Aluminum Area | mm² | 100
Over all conductor geometric area | mm² | 100
No and diameter of individual wire | No/mm | 7/3.56
Overall diameter | mm | 13.2
Max DC resistance at 20°C | Ω/km | 0.367
Ultimate Tensile Strength (UTS) | kN | 32
Weight | kg/Km | 585
Max current rating | Amp | 260
Temprature range | °C | -40 to +90
Humidity | % | 95
Drum
- Max drum wound lengths | M | 500
- Dimension (diameter * width ) | mm * mm | 1200*400
- Gross weight | kg | 1400
Conductor length per drum | mt | 500

## Straded Bare Copper Conductor
Mini Grid Project
Guaranteed Technical Parameters
Stranded Bare Copper Conductor
No | Description |  | Unit | Guaranteed Value
|  |  |  | Required | Offered
1 | Manufacturer
2 | Country of Origin
3 | Type designation
4 | Standard |  | IEC | IEC 60228
5 | Overall diameter, |  | mm | 8.7
6 | Cross section, |  | mm | 35
7 | No of Strand |  |  | 7
8 | Diameter of strand, |  | mm | 1.25
9 | DC resistance at 200C, |  | ohm/km | 0.535
10 | Continuous current carrying capacity, |  | A | 125
11 | Weight, |  | kg/km | 290
12 | Modules of elasticity, |  | kpa | 120000
13 | Rated tensile strength, |  | kN | 17.5
14 | Coefficient of linear expansion |  | Per 0C | 16.6x10 -6
15 | Standard delivery length per reel, |  | m | 500
16 | Overall reel dimensions, m | - Diameter | mm | 1200
17 |  | -Width | mm | 300
18 | Approximate gross weight of reel, |  | kg | 1000
19 | Net weight of Copper/Coil |  | kg | 150

## ABC
Mini Grid Project
Guaranteed Technical Parameters
Aerial Bundle Cable
No | Item | Unit | Guaranteed Value
|  |  | Required | Offered | Required | Offered | Required | Offered | Required | Offered | Required | Offered
| Description |  | 16mm conductor |  | 25mm conductor |  | 25mm messenger |  | 35mm conductor |  | 50mm conductor
1 | Manufacturer
2 | Country of manufacture
3 | Type
4 | Standard | IEC | IEC 60502-2 |  | IEC 60502-2 |  | IEC 60502-2 |  | IEC 60502-2 |  | IEC 60502-2
| Insulation |  | black extruded XLPE |  | black extruded XLPE |  | black extruded XLPE |  | black extruded XLPE |  | black extruded XLPE
| Conductor temperature for continuous operation | °C | 90 |  | 90 |  | 90 |  | 90 |  | 90
| Conductor temperature for 1 second during short circuit | °C | 250 |  | 250 |  | 250 |  | 250 |  | 250
5 | Rated voltage (Ph-N/Ph-Phase) | kV | 0.6 / 1 |  | 0.6 / 1 |  | 0.6 / 1 |  | 0.6 / 1 |  | 0.6 / 1
6 | Nominal phase to phase voltage | kV | 0.44 |  | 0.44 |  | 0.44 |  | 0.44 |  | 0.44
7 | One minute voltage test at 50hz | kV | 4 |  | 4 |  | 4 |  | 4 |  | 4
8 | Impulse withstand voltage 1.2 x 50 μs | kV | 20 |  | 20 |  | 20 |  | 20 |  | 20
9 | Cross section | mm² | 16 |  | 25 |  | 25 |  | 35 |  | 50
| Conductor type |  | Aluminum |  | Aluminum |  | Al-Alloy |  | Aluminum |  | Aluminum
10 | Permissible Continuous Current rating at 30°C ambient temprature | A | 85 |  | 110 |  | 110 |  | 135 |  | 170
11 | Rated DC resistance at 20°C | Ω/km | 1.91 |  | 1.2 |  |  |  | 0.868 |  | 0.641
12 | Diameter over bare conductor/messenger | mm | 4.4 |  | 5.8 |  | 5.8 |  | 6.8 |  | 8
13 | Inductive reactance | Ω/km | 0.11 |  | 0.085 |  | 0.085 |  | 0.07 |  | 0.058
14 | Average insulatation thickness | mm | 1.2 |  | 1.2 |  | 1.2 |  | 1.4 |  | 1.4
15 | Nominal diameter over insulation | mm | 6.8 |  | 8.2 |  | 8.2 |  | 9.6 |  | 10.8
16 | Tensile strength | N/mm² | 120 |  | 120 |  | 304 |  | 120 |  | 120
17 | Length of cable per drum | km | 500-1000 |  | 500-800 |  | 500-800 |  | 300-500 |  | 250-400
18 | Gross weight of Cable per drum | kg | 550-650 |  | 850-1000 |  | 850-1000 |  | 1150-1400 |  | 1450-1800
19 | Net weight of cable per drum | kg | 500-600 |  | 800-950 |  | 800-950 |  | 1100-1300 |  | 1400-1700
72

## Service Cable
Mini Grid Project
Guaranteed Technical Parameters
Copper Concentric Consumer Service Cables
No | Item | Unit | Guaranteed Value
|  |  | Required | Offered | Required | Offered | Required | Offered | Required | Offered | Required | Offered | Required | Offered | Required | Offered
1 | Manufacturer
2 | Catalogue No
3 | Manufacturer's Description if Item
4 | Country of Origin
| IEC Standard | IEC | IEC 60502-1 |  | IEC 60502-1 |  | IEC 60502-1 |  | IEC 60502-1 |  | IEC 60502-1 |  | IEC 60502-1 |  | IEC 60502-1
5 | Cable Type - No of cores X number of conductors / cross section mm2: | mm2 | 1X6/6 |  | 1X10/10 |  | 1x16/16 |  | 3X6/6 |  | 3X10/10 |  | 3x16/16 |  | 3x25/25
6 | Conductor and screem Material |  | Cu |  | Cu |  | Cu |  | Cu |  | Cu |  | Cu |  | Cu
7 | Imax 30°C ambient conductor 70°C | A | 45 |  | 64 |  | 83 |  | 135 |  | 198 |  | 270 |  | 375
8 | Conductor Insulation Material |  | PVC |  | PVC |  | PVC |  | PVC |  | PVC |  | PVC |  | PVC
9 | Outer sheath covering material |  | PVC |  | PVC |  | PVC |  | PVC |  | PVC |  | PVC |  | PVC
10 | Outer sheath colour |  | Black |  | Black |  | Black |  | Black |  | Black |  | Black |  | Black
11 | No of strands of phase conductor: | No | 7 |  | 10 |  | 14 |  | 21 |  | 30 |  | 42 |  | 60
12 | No of strands of neutral concentric conductor: | No | 19 |  | 19 |  | 19 |  | 19 |  | 19 |  | 19 |  | 19
13 | Nominal thickness of insulation, | mm | 0.6 |  | 0.6 |  | 0.6 |  | 0.6 |  | 0.6 |  | 0.6 |  | 0.6
14 | Nominal thickness of outer sheath, | mm | 1.2 |  | 1.2 |  | 1.2 |  | 1.2 |  | 1.2 |  | 1.2 |  | 1.2
15 | Max phase conductor dc resistance at 20 °C: | Ω/km | 3.08 |  | 1.83 |  | 1.14 |  | 3.08 |  | 1.83 |  | 1.14 |  | 0.73
16 | Max neutral conductor dc resistance at 20 °C: | Ω/km | 1.26 |  | 0.75 |  | 0.47 |  | 1.26 |  | 0.75 |  | 0.47 |  | 0.31
17 | Phase AC resistance (max) | ohm/km | 3.56 |  | 2.06 |  | 1.32 |  | 3.56 |  | 2.06 |  | 1.32 |  | 0.89
18 | Equivalent 3phase star reactance @50Hz | mohm/km | 0.035 |  | 0.028 |  | 0.021 |  | 0.035 |  | 0.028 |  | 0.021 |  | 0.016
19 | Maximum electrost. Capacity of cable | pF/core | 100 |  | 100 |  | 100 |  | 100 |  | 100 |  | 100 |  | 100
20 | Design & Normal working voltage (Eo/E) | V | 0.6/1 |  | 0.6/1 |  | 0.6/1 |  | 0.6/1 |  | 0.6/1 |  | 0.6/1 |  | 0.6/1
21 | Power Frequency Withstand, 1 min | kV | 3.5 |  | 3.5 |  | 3.5 |  | 3.5 |  | 3.5 |  | 3.5 |  | 3.5
22 | Short circuit current carrying capacity | kA at 1 sec | 3.4 |  | 3.4 |  | 3.4 |  | 3.4 |  | 3.4 |  | 3.4 |  | 3.4
23 | Minimum breaking stress | N/mm2 | 100 |  | 100 |  | 100 |  | 100 |  | 100 |  | 100 |  | 100
24 | Max Operating Temperature | oC | 70 |  | 70 |  | 70 |  | 70 |  | 70 |  | 70 |  | 70
25 | Nominal weight per meter of completed cable | Kg/m | 0.32 |  | 0.45 |  | 0.59 |  | 0.85 |  | 1.26 |  | 1.68 |  | 2.36
26 | Max spacing distance of marking | m | 2 |  | 2 |  | 2 |  | 2 |  | 2 |  | 2 |  | 2
27 | Drum length | m | 500 |  | 500 |  | 500 |  | 500 |  | 500 |  | 500 |  | 500
28 | Drum weight | Kg | 40 |  | 60 |  | 90 |  | 120 |  | 160 |  | 220 |  | 300
29 | Cable identification per spec |  | As per IEC 60502-1 |  | As per IEC 60502-1 |  | As per IEC 60502-1 |  | As per IEC 60502-1 |  | As per IEC 60502-1 |  | As per IEC 60502-1 |  | As per IEC 60502-1

## Galvanized Steel Wire
Mini Grid Project
Guaranteed Technical Parameters
Galvanized steel wire 7 x 2.65 mm2
No | Description | Unit | Guaranteed Value
|  |  | Required | Offered
1 | Manufacturer
2 | Country of origin
3 |  | IEC | IEC 60888 / IEC 61089
4 | Type designation |  | Galvanized steel wire
5 | Diameter of wire | mm | 2.65
6 | No of stranded |  | 7
7 | Breaking load | KN | 40
8 | Tensile Strength | N/mm2 | 1570
9 | Thickness of Zinc coating | µm | 260g/m2
10 | Length of stranded per coil | mt | 1000
11 | Net weight per coil | kg | 150

## Aluminum Tie Wire
Mini Grid Project
Guaranteed Technical Parameters
Aluminum Round Tie Wire
No | Description | Unit | Guaranteed Value
|  |  | Required | Offered
1 | Manufacturer
2 | Country of origin
3 | IEC Standards | IEC | IEC 61089
4 | Type designation |  | Aluminium Round tie wire
5 | Material designation according to IEC |  | Aluminium 1350 (99.5% Purity)
6 | Diameter of wire | mm | 2.5
7 | Breaking load | KN | >4.5
8 | Tensile Strength | N/mm2 | >110
9 | Length of stranded per coil | m | 500
10 | Net weight per coil | kg | 8.4

## 11 kV Distribution Transformer
Mini Grid Project
Guaranteed Technical Parameters
11/0.4 kV Transformers
Item | Unit | Guaranteed Value
|  | Required | Offered
I. General
Manufacturer
IEC Standard | IEC 60076 | IEC 60076-Part 24, IEC 60296, IEC 60038
Country of manufacture
Kind of installation |  | Outdoor
Pole mounted
No. of phases |  | Three-phase
Type of tank |  | Bolted Cover
No. of windings |  | Two
Vector group symbol |  | Dyn11
Tapping range | ± % | 2.5
Number of steps | ± steps | +2, -2
Continuous power at all taps |  | Yes
Cooling method |  | ONAN
Specification of oil ( 60296) |  | IEC 60296
II. Ratings
Rated power | kVA | 50
Nominal system voltage
primary UN1 | kV | 11
secondary UN2 | kV | 0.4
Frequency | Hz | 50
Principal tapping | kV | 11
Maximum Continuous System withstand Voltage | kV | 12
Impedance voltage at rated power | % | 4.5
HV Windings
Material, wire or strip |  | Copper wire
Insulation |  | Kraft Paper + mineral Oil
Power frequency withstand voltage, kV(rms) | kV(rms) | 28 (IEC) / 70†
Rated lightning, impulse withstand voltage, kV(peak) | kV(peak) | 75 (IEC) / 170†
LV Windings
Material, wire or strip |  | Copper wire
Insulation |  | Class B
Magnetic flux density (at rated voltage and frequency) | Tesla | max. 1.65
Core Material |  | CRGO
Core Loss figure, Watt/kg |  | 0.5-1.5
III. Operation Details
Ambient temperature (max.) | °C | 45
Ambient temperature (average) | °C | 30
Temperature rise limit (at 1000 m ) |  | ≤65
oil / top | °C | 55
windings / average | °C | 60
windings hot spot | °C | 68
No-load loss at rated voltage and frequency | W | ≤180
Full load loss ,W | W | ≤950
Rated voltage at full load (P.F=0.95) | kV | 0.4
Efficiency referred to 75oC at rated voltage and frequency |  | ≥ 0.975
No load current as percent of rated current |  | <3%
at 90% voltage (%) |  | 0.015
at 100% voltage (%) |  | 0.02
IV. Bushings
Primary
manufacturer
rated current | A | 5
power frequency test level (at 1000 m) | kV | 28
lightning impulse level (at 1000 m) | kV | 75
clearance across insulator (at 1000m) | mm | As per (IEC 60076)
adjustable arcing horns | Each | As per (IEC 60076)
creepage distance | mm | 320
Secondary
Manufacturer
type (DIN type or eqvt.) |  | IEC 60076-1
rated current | A | 72
power frequency test level (at 1000 m) | kV | min. 0.8KV
lightning impulse level (at 1000 m) | kV | 3
clearance across insulator | mm | As per (IEC 60076)
Min. creepage distance | mm | 250
V. Tests
Routine tests: IEC 60076 and Specifications |  | As per (IEC 60076)
Separate source over-voltage withstand test |  | As per (IEC 60076)
Induced overvoltage withstand test, |  | As per (IEC 60076)
test voltage / primary (tap 1) (IEC test standard) | kV | As per (IEC 60076)
test voltage / secondary (IEC test standard) | kV | As per (IEC 60076)
Type tests: IEC 60076 and Specifications |  | As per (IEC 60076)
test voltage / full wave (IEC test standard) | kV | As per (IEC 60076)
test voltage / chopped wave (IEC test standard) | kV | As per (IEC 60076)
Heat-run test |  | As per (IEC 60076)
Noise level at a measuring distance of 0.3 m | dB(A) | As per NEMA ST-20
VI. Materials, Masses, Measures and Drawings
Transformer tank,material |  | Steel/Hot-dip galvanized
Transformer total mass | kg | 200-350
Overall dimensions including bushings:
height | mm | 800-1000
depth | mm | 800-900
width | mm | 600-700
Thickness of tank plate
Top, mm | mm | 3
Bottom, mm | mm | 5
Sides, mm | mm | 4
Colour of transformer |  | Grey
Thickness of surface treatment | µm | ≥80
Drawing of dimensions | No. | 3
Pamphlet | No. | 2

## Composite Insulator
Mini Grid Project
Guaranteed Technical Parameters
11kV Composite Tension Insulator
Description | Unit | Guaranteed Value
|  | Required | Offered
Name of manufacturer
Country of manufacture
Material |  | Composite
IEC Standard | IEC | IEC 60305 , IEC 60120 IEC 60815
Mounting |  | Vertical or Horizontal
Core diameter. | mm | 16
Shed diameter max. | mm | 90
Shed spacing min. | mm | 55
Number of sheds |  | 4 to 6
Ratio between creepage distance and clearance | mm | ≥2.5
Inclination of sheds | Degree | 25 to 45
Length | mm | 450
Dimension metal fitting | mm | As Per IEC 60120 -(16-20)
Rated creepage distance min. | mm | As Per IEC 60815 -(≥275)
Creepage factor | mm/kV | ≥25
Profile |  | Aerodynamic/Alaternating shed
Power frequency withstand voltage: | kVrms
· dry |  | 75
· wet |  | 35
Impulse withstand voltage (1.2/50μs), (positive). | kVpeak | ≥75
Mechanical failing load | kN | ≥45
Sample image item submitted | Yes/no | yes
Net weight | kg | 1.5 - 2.5
Package type |  | wooden/corrugated box
Number of insulator per package | no | <100
Package type |  | wooden/corrugated box
Guarantee |  | 12 months from commisisoning or 18 months from date of last dispatch
11kV Disc Insulator
Description | Unit | Guaranteed Value
|  | Required | Offered
Name of manufacturer
Country of manufacture
Type of insulator |  | Polymeric Composite Disc
IEC Standard | IEC | IEC 61109, 60071-1, IEC 60038
Materials of FRP Rod |  | Boron free ECR
Materials of sheds |  | Silicon rubber
Type of metal end fittings |  | Tongue & Clevis
Material of end fittings |  | SGCI/MCI
Material of sealing compound |  | RTV Silicon
Colour of sheds |  | Grey
Rated Voltage | kV | 1 1
Highest Voltage | kV | 12
Diameter of FRP rod | mm | 16
Diameter of weather sheds | mm | 100
Length of FRP rod (min) | mm | 200
Thickness of housing | mm | 3
Dry arc distance | mm | 170
Method of fixing sheds to housing |  | injection moulding
No. of weather sheds(min) |  | three
Dry Power Frequency withstand Voltage | kV | 60
Visible Discharge voltage (PF) | kV | 9
Wet Power Frequency Flashover Voltage | kV | 45
RIV at 1MHz when energized at 10kV/ 30kV (rms) under dry condition |  | <50 microvolt
Power frequency withstand voltage: | kVrms
· dry |  | 75
· wet |  | 35
Creepage distance (min) | mm | ≥320
Mechanical failing load | kN | ≥45
Sample image item submitted | Yes/no
Number of insulator per package | no | <100
Package type |  | wooden/corrugated box
Guarantee |  | 12 months from commisisoning or 18 months from date of last dispatch
11kV Pin Insulator
Description | Unit | Guaranteed Value
|  | Required | Offered
Name of manufacturer
Country of manufacture
Type of insulator |  | Polymeric Composite Pin
IEC Standard | IEC | IEC 61109, IEC 60071-1, IEC 60038
Materials of FRP Rod |  | Boron free ECR
Materials of sheds |  | Silicon rubber
Material of bottom end fittings |  | Forged steel
Material of top end fittings |  | SGCI/MCI/forged steel
Material of sealing compound |  | RTV Silicon
Colour of sheds |  | Grey
Rated Voltage | kV | 1 1
Highest Voltage | kV | 12
Diameter of FRP rod | mm | 20
Diameter of weather sheds | mm | 100
Length of FRP rod (min) | mm | 165
Thickness of housing | mm | 3
Thread length of bottom end fitting (min) | mm | 110
Diameter of bottom end fitting | mm | 20
Dry arc distance | mm | 150
Method of fixing sheds to housing |  | injection moulding
No. of weather sheds(min) |  | three
Dry Power Frequency withstand Voltage | kV | 60
Dry Lightning Impulse withstand volatge | kV | Positive: 75
Negative: 80
Dry Lightning Impulse flashover voltage | kV | Positive: 95
Negative: 100
Visible discharge voltage (PF) | kV | 9
Wet Power Frequency Flashover Voltage | kV | 45
RIV at 1MHz when energized at 10kV/ 30kV (rms) under dry condition |  | <50 microvolt
Power frequency withstand voltage: | kVrms
· dry |  | 75
· wet |  | 35
Creepage distance (min) | mm | 320
Mechanical failing load | kN | 45
Sample image item submitted | Yes/no
Number of insulator per package | no | <100
Package type |  | wooden/corrugated box
Guarantee |  | 12 months from commisisoning or 18 months from date of last dispatch

## Concrete Poles
Mini Grid Project
Guaranteed Technical Parameters
Concrete Poles
Description | Unit | Guaranteed Value
|  | Required | Offerred
IEC Standarrd | IEC | IEC 60652
Pole Type | - | B11-800, A11-300
Material | - | Reinforced Concrete
Overall Length | m | 11
Load Capacity (Ultimate Bending Moment) | kNm | 80
Load Capacity (Working Load at 0.6m from top) | kN | As per design
Top Diameter | mm | 190 – 220 (Approx.)
Bottom Diameter | mm | 350 – 400 (Approx.)
Wall Thickness | mm | 25 – 50 (as per design)
Reinforcement Type | - | High Tensile Steel
Prestressing Wire | mm | 5 – 10 mm dia. (as per requirement)
Concrete Strength (at 28 days) | MPa | ≥ 45
Service Life | Years | ≥ 50
Mounting Type | - | Directly Buried
Burial Depth | m | ~ 1.8 – 2.0
Weight | kg | Approx. 800 – 1000
Standard Compliance | - | IEC 60652 / National Standards
Surface Treatment | - | Smooth Finish with Curing
Pole Marking | - | Engraved/Embossed as per spec
Description | Unit | Guaranteed Value
|  | Required | Offerred
Pole Type | - | B10-500
Material | - | Reinforced Concrete
Overall Length | m | 10
Load Capacity (Ultimate Bending Moment) | kNm | 50
Load Capacity (Working Load at 0.6m from top) | kN | As per design
Top Diameter | mm | 180 – 200 (Approx.)
Bottom Diameter | mm | 300 – 350 (Approx.)
Wall Thickness | mm | 25 – 50 (as per design)
Reinforcement Type | - | High Tensile Steel
Prestressing Wire | mm | 5 – 10 mm dia. (as per requirement)
Concrete Strength (at 28 days) | MPa | ≥ 45
Service Life | Years | ≥ 50
Mounting Type | - | Directly Buried
Burial Depth | m | ~ 1.5 – 1.8
Weight | kg | Approx. 500 – 800
Standard Compliance | - | IEC 60652
Surface Treatment | - | Smooth Finish with Curing
Pole Marking | - | Engraved/Embossed as per spec

## Composite Post Insulator
Mini Grid Project
Guaranteed Technical Parameters
11kV Composite Post Insulator
No. | Description | Unit | Guaranteed Value
|  |  | Required | Offered
Name of manufacturer
Country of manufacture
| Type |  | HTV Silicon rubber, fibreglass rod
| Standard |  | IEC 61109 / IEC 61952
| Mounting |  | vertical
| Core diameter. | mm | 16-22
| Shed diameter min. | mm | ≥90
| Shed spacing min. | mm | 40-55
| Number of sheds |  | 6 to 10
| Ratio between creepage distance and clearance | mm | ≥2
| Inclination of sheds | mm | Alternating or downward tilted (≤ 45° from vertical)
| Length | mm | 330-380
| Dimension metal fitting | mm | As per IEC Type C -(16-20)
| Rated creepage distance min. | mm | ≥275
| Creepage factor |  | ≥25
| Profile |  | smooth/alternate
| Power frequency withstand voltage: | kVrms
| · dry |  | ≥ 45
| · wet |  | ≥ 35
| Impulse withstand voltage (1.2/50μs), pos. | kVpeak | ≥ 75
| Ultimate bending stress (cantilever) | kN | ≥5
Conductor grooves:
| · For side tie attachment of the conductor by prefabricated wrap locked ties |  | Tie Type
| · For clamp-top type (turin type) |  | Clamp Type
| Sample item shall be submitted | Yes/no | yes
| Net weight | kg | 0.8-1.2
| Package type |  | wooden/corrugated box
| Number of insulator per package | no | <100

## U-Channel Cross Arm
Guaranteed Technical Parameters
U Channel Cross Arm (Suspension & Light Angle)
No. | Description | Unit | Required | Offered
1 | - Manufacturer
2 | - Country of origin
3 | - Manufacturing capacity per month
4 | IEC Standards | IEC | IEC 60652, ISO 1461
5 | Tensile strength (N/mm2) | N/mm² | ≥410
6 | - Yield strength of U-cross arm (N/mm2) | N/mm² | ≥250
7 | - Complete dimension of U-cross arm for suspension, dead end , and T-off
| a. Length (mm) | mm | 1200
| b. Width (mm) | mm | 75
| c. Depth (mm) | mm | 40
| d. Thickness (mm) | mm | 5
8 | - Galvanization |  | Hot dip galvanized
9 | - Thickness of galvanization (mm) | µm | 85
10 | - Net weight per piece (kg) | kg | 6 to 8
11 | -Size and no. of pre galvanized drilled holes |  | Ø18 mm holes, 6–8 holes
12 | Sample photo item shall be submitted (yes/no) |  | yes
Guaranteed Technical Parameters
Medium Voltage Cross Arm (Heavy Angle Tension)
No. | Description | Unit | Required | Offered
1 | - Manufacturer
2 | - Country of origin
3 | - Manufacturing capacity per month
4 | IEC Standard applied |  | IEC 60652, ISO 1461, IEC 62217
5 | Tensile strength (N/mm2) |  | ≥410
6 | - Yield strength of U-cross arm (N/mm2) | N/mm² | ≥250
7 | - Complete dimension of U-cross arm for heavy angle
| a. Length (mm) | mm | 1500
| b. Width (mm) | mm | 100
| c. Depth (mm) | mm | 50
| d. Thickness (mm) | mm | 6
8 | - Galvanization |  | Hot dip galvanized as per ISO 1461
9 | - Thickness of galvanization (mm) | µm | ≥85
10 | - Net weight per piece (kg) |  | 10 to 12
11 | -Size and no. of pre galvanized drilled holes |  | Ø18 mm holes, 8–10 holes
12 | Sample photo item shall be submitted (yes/no) |  | yes
Guaranteed Technical Parameters
Medium Voltage Cross Arm (T-Off and Dead End)
No. | Description | Unit | Required | Offered
1 | - Manufacturer
2 | - Country of origin
3 | - Manufacturing capacity per month
4 | IEC Standards |  | IEC 60652 (mechanical testing), ISO 1461, IEC 62217
5 | Tensile strength (N/mm2) |  | ≥410
6 | - Yield strength of U-cross arm (N/mm2) |  | ≥250
7 | - Complete dimension of U-cross arm for heavy angle
| a. Length (mm) |  | 1600
| b. Width (mm) |  | 100
| c. Depth (mm) |  | 50
| d. Thickness (mm) |  | 6
8 | - Galvanization |  | Hot dip galvanized as per ISO 1461
9 | - Thickness of galvanization (mm) | µm | ≥85
10 | - Net weight per piece (kg) |  | 11 to 13
11 | -Size and no. of pre galvanized drilled holes |  | Ø18 mm holes, 10–12 holes
12 | Sample photo item shall be submitted (yes/no) |  | yes
Guaranteed Technical Parameters
Cross Arm for Transformer Base
No. | Description | Unit | Required | Offered
1 | - Manufacturer |  | To be provided
2 | - Country of origin |  | To be provided
3 | - Manufacturing capacity per month |  | To be provided
4 | IEC Standards |  | IEC 60652 (mechanical testing), ISO 1461 (galvanization), IEC 61952/IEC 62217
5 | Tensile strength (N/mm2) |  | ≥410
6 | - Yield strength of U-cross arm (N/mm2) |  | ≥250
7 | - Complete dimension of U-cross arm for suspension, Heavy angle ,Dead end , and T-off
| a. Length (mm) |  | 1800
| b. Width (mm) |  | 100
| c. Depth (mm) |  | 50
| d. Thickness (mm) |  | 6
8 | - Galvanization |  | Hot dip galvanized as per ISO 1461
9 | - Thickness of galvanization (mm) | µm | ≥85
10 | - Net weight per piece (kg) |  | 12 to 14
11 | -Size and no. of pre galvanized drilled holes |  | Ø18 mm, 10–14 holes
12 | Sample photo item shall be submitted (yes/no) |  | yes
Guaranteed Technical Parameters
M16, 300mm, Long bolt with Nut and Washer
No. | Description | Unit | Required | Offered
1 | - Manufacturer
2 | - Country of origin
3 | - Manufacturing capacity per month
4 | IEC Standards |  | IEC 61284, ISO 898-1 (Mechanical strength of fasteners), ISO 4032 (Hex nuts), ISO 1461 (Galvanization),
5 | Material |  | Galvanized steel
6 | Tensile strength (N/mm2) | N/mm² | ≥410
7 | - Yield strength of round iron bar (N/mm2) | N/mm² | ≥250
8 | - Complete dimension of long bolt for fixing U-cross arm on the pole
| a. Length (mm) | mm | 300
| b. Rod diameter (mm) | mm | 16
| c. Thread nominal diameter |  | M16
| d. Threaded length of the rod | mm | 80
| e. Required Number of nuts for each bolt |  | 2
| f. Required Number of washer for each bolt |  | 2
| g. Washer inside and outside diameter |  | As per IEC standards
| h. Washer thickness |  | As per IEC standards
9 | - Galvanization |  | Hot dip galvanized as per ISO 1461
10 | - Thickness of galvanization (mm) | µm | ≥85
11 | - Net weight per piece (kg) |  | 0.75-0.9
12 | -Size | mm | 16mm dia with 300mm long
13 | Sample photo item shall be submitted (yes/no) |  | yes
Guaranteed Technical Parameters
M20, 400mm Long Bolt with Nut and Washer
No. | Description | Unit | Required | Offered
1 | - Manufacturer
2 | - Country of origin
3 | - Manufacturing capacity per month
4 | IEC Standards |  | IEC 61284, ISO 1461 (Galvanization), ISO 898-1 (Mechanical properties of fasteners), ISO 4032 (Hex nuts)
5 | Material |  | Galvanized steel
6 | Tensile strength (N/mm2) | N/mm² | ≥410
7 | - Yield strength of round iron bar (N/mm2) | N/mm² | ≥250
8 | - Complete dimension of long bolt for fixing transformer base U-cross arm on the pole
| a. Length (mm) | mm | 400
| b. diameter (mm) | mm | 20
| c. Thread nominal diameter(mm) |  | M20
| d. Threaded length of the rod(mm) | mm | 100
| e. Required Number of nuts for each bolt |  | 2
| f. Required Number of washer for each bolt |  | 2
| g. washer inside and outside diameter |  | As per IEC standard
| h. Washer thickness |  | As per IEC standard
9 | - Galvanization |  | Hot dip galvanized as per ISO 1461
10 | - Thickness of galvanization (mm) | µm | ≥85
11 | - Net weight per piece (kg) |  | 1.2-1.5
12 | -Size |  | 20mm dia with 400mm long
13 | Sample photo item shall be submitted (yes/no) |  | yes
Guaranteed Technical Parameters
Bolt and nut M10, 40mm
No. | Description | Unit | Required | Offered
1 | - Manufacturer
2 | - Country of origin
3 | - Manufacturing capacity per month
4 | IEC Standards |  | IEC 61284, SO 898-1 (Mechanical properties of fasteners), ISO 4032 (Nuts), ISO 7089 (Washers), ISO 1461 (Galvanization), IEC 61284
5 | Material |  | Galvanized steel
6 | Tensile strength (N/mm2) | N/mm² | ≥410
7 | - Yield strength of round iron bar (N/mm2) | N/mm² | ≥250
8 | - Complete dimension of the bolt for fixing tie strap on U-cross arm
| a. Length (mm) | mm | 40
| b. diameter (mm) |  | M10
| Threaded length of the rod (mm) | mm | ≥25
| c. Required Number of nuts for each bolt (each) |  | 1
| d. Number of washers required for each bolt (each) |  | 2
9 | - Galvanization |  | Hot dip galvanized as per ISO 1461
10 | - Thickness of galvanization (mm) | µm | ≥70
11 | - Net weight per piece (kg) |  | 0.08-0.1
Guaranteed Technical Parameters
Tie Strap 5x50x900 mm
No. | Description | Unit | Required | Offered
1 | - Manufacturer
2 | - Country of origin
3 | - Manufacturing capacity per month
4 | IEC Standards |  | IEC 61284, ISO 630 (Structural steel), ISO 1461 (Galvanization)
5 | Tensile strength (N/mm2) | N/mm² | ≥410
6 | - Yield strength of Tie strap (N/mm2) | N/mm² | ≥250
7 | - Complete dimension of Tie strap
| a. Length (mm) | mm | 900
| b. Width (mm) | mm | 50
| c. Thickness (mm) | mm | 5
8 | - Galvanization |  | Hot dip galvanized as per ISO 1461
9 | - Thickness of galvanization (mm) | µm | 85
10 | - Net weight per piece (kg) |  | 1.8-2.1
Guaranteed Technical Parameters
Strain Clamp
No. | Description | Unit | Required | Offered
1 | Manufacturer
2 | Country of origin
3 | Standards |  | IEC 61284, ISO 1461 (Galvanization), ISO 898-1 (Bolts)
4 | Range of conductor diameter (mm) |  | 6 to 16
5 | Material |  | Aluminum Alloy
| a. Body and keeper |  | Aluminum Alloy
| b. Cotter pin ᶲ16 and |  | Galv. Forged steel
| c. Plain washer ᶲ16 |  | Galvanized steel to ISO 7089
6 | Material standard |  | EN 10025 / ISO 630 for steel, ASTM B108 for aluminum
7 | Size |  | 16 to 30
8 | Minimum failing load (KN) | kN | ≥40
9 | Strength class of bolts |  | Class 8.8 or higher (as per ISO 898-1)
10 | Tightening torque of bolts (N-m) | Nm | 50-60
11 | Thickness of zinc coating, (mm) | µm | ≥ 85
12 | Net weight per piece, (kg) |  | 1.5-2.5
Guaranteed Technical Parameters
Socket Eye
No. | Description | Unit | Required | Offered
1 | Manufacturer
2 | Country of origin
3 | IEC Standards |  | ISO 683 (Heat-treated steels), ISO 630 (Structural steels), IEC 61284 (Overhead line fittings), IEC 120 (Coupling dimensions)
4 | Material standard |  | Forged steel
5 | Mechanical failing load |  | BS 3288
6 | Mechanical routine test load (KN) | kN | ≥ 70
7 | Diameter of eye (KN) | kN | ≥ 50
8 | Size of coupling according to IEC 120 (mm) | mm | As per IEC 120 standard (16-20)
9 | Thickness of zinc coating (mm) |  | ≥ 85
10 | Net weight per piece (mm) |  | 0.8-1.5
Guaranteed Technical Parameters
Small Collar
No. | Description | Unit | Required | Offered
1 | - Manufacturer
2 | - Country of origin
3 | - Manufacturing capacity per month
4 | IEC Standards |  | IEC 61284 (Overhead Line Fittings), ISO 630 (Structural Steel), ISO 1461 (Hot-Dip Galvanization)
5 | Material |  | Hot deep galvanized steel
6 | Tensile strength (N/mm2) | N/mm² | ≥410
7 | - Yield strength of round iron bar (N/mm2) | N/mm² | ≥250
| a. Length (mm) | mm | 50-80
| b. diameter (mm) |  | 16/20
| c. Thread nominal diameter |  | M16 /M20
| d. Threaded length on each leg | mm | 20-40
| e. Required Number of nuts on each leg |  | 2
| f. Required Number of washer for each bolt |  | 2
| g. washer inside and outside diameter |  | As per IEC standard
| h. Washer thickness |  | As per IEC standard
9 | - Finished galvanization |  | Hot deep galvanization As per ISO 1461
10 | - Thickness of galvanization (mm) | µm | ≥ 85
11 | - Net weight per piece (kg) |  | 0.25-0.4
Guaranteed Technical Parameters
Cable lug
* This will be supplied with the specified transformers so it is considered as a part of the transformer and its type is as per stated on the technical specification
Guaranteed Technical Parameters
Bolted Parallel Groove Clamp
No | Description | Unit | Required | Offered
1 | Manufacturer
2 | Country of origin
3 | Type designation
4 | IEC Standards |  | IEC 61284, IEC 1238-1, ISO 898-1, ISO 1461
5 | Range of main conductor cross section, | mm2 | Al 16…120mm2
6 | Range of branch conductor cross section, | mm2 | Al 16…120mm2
| Material of main conductor, |  | Aluminum Alloy
7 | Material of branch conductor, |  | Aluminum Alloy
9 | Tensile strength, | N/mm2 | ≥ 240
10 | Thread size of bolt and nut |  | M10 or M12
| Number of bolts and nuts per clamp | each | 2bolts & 2nuts
11 | Thickness of zinc coating, | μm | >8
12 | Net weight per piece, | kg | 0.4-0.8
Guaranteed Technical Parameters
Parallel Groove Clamps Al/Al 25…160 mm2
No | Description | Unit | Required | Offered
1 | Manufacturer
2 | Country of origin
3 | IEC Standards |  | IEC 61284, IEC 1238-1 , ISO 1461
4 | Range of main conductor cross-section | mm2 | Al 25…160mm2
5 | Range of branch conductor cross-section | mm2 | Al 25…160mm2
6 | Range of main conductor diameter | mm | 6 to 18
7 | Range of branch conductor diameter | mm | 6 to 18
8 | Material of main conductor |  | Aluminum alloy
9 | Material of branch conductor |  | Aluminum alloy
10 | Tensile strength of the body | N/mm2 | ≥ 240
11 | Strength class of bolts and nuts
12 | Thread size of bolts and nuts |  | M10 or M12
13 | Tightening torque of bolts | Nm | 40
14 | Thickness of zinc coating | mm | 85
15 | Net weight per piece | g | 0.5-0.9
Guaranteed Technical Parameters
Parallel Groove Clamps Al 25…200 mm2/Cu 10…120 mm2
No | Description | Unit | Required | Offered
1 | Manufacturer
2 | Country of origin
3 | IEC Standards |  | IEC 61284 / EN 50483
4 | Type Designation |  | Parallel Groove Clamp Al/Cu
5 | Range of main conductor cross-section | mm2 | Al 25…200mm2
6 | Range of branch conductor cross-section | mm2 | Cu 10…120 mm2
7 | Range of main conductor diameter | mm | 6 to 18
8 | Range of branch conductor diameter | mm | 4 to 13
9 | Material of main conductor |  | Aluminum Alloy
10 | Material of branch conductor |  | Copper
12 | Tensile strength of the body | N/mm2 | ≥ 160
13 | Strength class of bolts and nuts |  | 8.8 grade steel
14 | Thread size of bolts and nuts |  | M8 or M10
15 | Tightening torque of bolts | Nm | 20-25
16 | Thickness of zinc coating | mm | ≥ 0.08
17 | Net weight per piece | g | 0.45-0.6
Guaranteed Technical Parameters
Mid span joint for AAAC 95 mm2
No | Description | Unit | Required | Offered
1 | Manufacturer
2 | Country of origin
3 | IEC Standards | IEC | IEC 60104 / EN 50182
6 | Material of main conductor |  | Aluminum Alloy
8 | Tensile strength of the body | N/mm2 | ≥ 160
9 | Breaking load of joint (UTS) | KN | ≥ 31
10 | Thickness of zinc coating | µm | ≥ 80
11 | Net weight per piece | Kg | 0.35-0.45
Guaranteed Technical Parameters
Ball Eye
No | Description | Unit | Required | Offered
1 | Manufacturer
2 | Country of origin
3 | IEC Standards | IEC | IEC 60120 / EN 61284
4 | Material |  | Forged steel
5 | Mechanical failing load | kN | ≥ 70
6 | Mechanical routine test load | kN | ≥ 50
7 | Diameter of eye | mm | 16
8 | Size of coupling according to IEC 120 | mm | 16
9 | Thickness of zinc coating | mm | ≥ 0.08
10 | Net weight per piece | kg | 0.6-0.8
Guaranteed Technical Parameters
Earth Rod and Clamp
No | Description | Unit | Required | Offered
1 | Manufacturer
2 | Country of origin
3 | IEC Standard | IEC | IEC 62561-2 / IEC 60364
5 | Material of rod and clamp |  | Copper-bonded steel rod and brass clamp
6 | Standard Reference |  | IEC 62561-2 (Lightning Protection System – Part 2: Earth Termination System Components)
7 | Material Standard |  | ASTM B843 (for copper bonding), BS 2874 (for clamp)
8 | Section profile | mm | Ø16
9 | Length of the rod | m | 1.5 or 2.4
10 | Net weight of rod and clamp per piece | g | 2.5-3.5
Guaranteed Technical Parameters
Suspension Clamp
No | Description | Unit | Required | Offered
1 | Manufacturer
2 | Country of origin
3 | IEC Standard |  | IEC 61284 / EN 50483-3
5 | Material |  | Aluminum alloy with galvanized steel bolts
6 | Material standard |  | EN AW-6060 / ISO 3506
7 | Range of conductor cross-section | mm2 | 16-95
8 | Range of conductor diameter | mm | 6-18
9 | Allowable Tensile strength for 25/35 mm2 messenger | kN | ≥ 9
| Allowable Tensile strength for 50 mm2 messenger | kN | ≥ 12.5
10 | Thickness of zinc coating | mm | ≥ 80
11 | Net weight per piece | kg | 0.8-1.2
Guaranteed Technical Parameters
Dead End Clamp
No | Description | Unit | Required | Offered
1 | Manufacturer
2 | Country of origin
3 | IEC Standard | IEC | IEC 61284 / EN 50483-4
5 | Material |  | Aluminum alloy with galvanized steel
7 | Range of conductor cross-section | mm2 | 16-95
8 | Range of conductor diameter | mm | 6 --18
| Allowable Tensile strength | kN | ≥ 15
10 | Thickness of zinc coating | mm | ≥ 80
11 | Net weight per piece | kg | 0.5-0.8
Guaranteed Technical Parameters
Insulation Piercing Clamps, Al/Cu
No | Description | Unit | Required | Offered
1 | Manufacturer
2 | Country of origin
3 | IEC Standard | IEC | IEC 61284 / EN 50483-4
4 | Material |  | Aluminum Alloy and insulating material
6 | Range of conductor cross-section | mm2 | 16…95 (main)/1.5…35 (tap)
7 | Range of conductor diameter, Al/Cu | mm | 4--18
8 | Tensile strength | kN | ≥ 4
9 | Thickness of zinc coating, | µm | ≥ 80
10 | Net weight per piece | Kg | 0.15-0.35
Guaranteed Technical Parameters
Insulation Piercing Clamps, Al/Al
No | Description | Unit | Required | Offered
1 | Manufacturer
2 | Country of origin
3 | IEC Standards | IEC | IEC 61284 / EN 50483-4
4 | Material |  | UV-resistant thermoplastic body, tin-plated aluminum teeth, stainless steel
6 | Range of conductor cross-section | mm2 | 16…95 (main)/16…95 (Tap)
7 | Range of conductor diameter, Al/Al | mm | 4.0-18.0
8 | Tensile strength | kN | ≥ 4
9 | Thickness of zinc coating, | µm | ≥ 80
| Test voltage at 50hz for one minute in water | KV | ≥ 6
10 | Net weight per piece | kg | 0.2-0.35
Guaranteed Technical Parameters
Suspension Hook, ABC, Normal Type I
No | Description | Unit | Required | Offered
1 | Manufacturer
2 | Country of origin
3 | Manufacturing capacity per month
4 | IEC Standard | IEC | IEC 61284 / ISO 898-1 / ISO 1461
5 | Yield strength of hook (N/mm2) | N/mm² | ≥ 240
6 | Complete dimension of hook
| a. Length | mm | 150-180
| b. Width | mm | 40-50
| c. Rod diameter | mm | 12
| d. Thread nominal diameter | mm | M12
| e. Thread minor diameter | mm | 10.2
| f. Washer outside and inside diameter | mm | As per IEC standard
| g. Washer thickness | mm | As per IEC standard
| h. Length of thread |  | Full thread
| i. Thread length | mm | ≥ 50
7 | Galvanization |  | Hot-dip galvanized
8 | Thickness of galvanization | mm | ≥ 80
9 | Net weight per piece | kg | 0.4-0.6
Guaranteed Technical Parameters
Suspension Hook, ABC Type II, (for LV under MV )
No | Description | Unit | Required | Offered
1 | Manufacturer
2 | Country of origin
3 | Manufacturing capacity per month
4 | IEC Standard | IEC | IEC 61284 / ISO 898-1 / ISO 1461
5 | Yield strength of hook | N/mm² | ≥ 240
6 | Complete dimension of hook
| a. Length | mm | 180-200
| b. Width | mm | 45-55
| c. Rod diameter | mm | 14
| d. Thread nominal diameter | mm | M14
| e. Thread minor diameter | mm | 12.1
| f. Washer outside and inside diameter | mm | As per IEC standard
| g. Washer thickness | mm | As per IEC standard
| h. Length of thread |  | 60-70
| i. Thread length | mm | 60
7 | Galvanization |  | Hot-dip galvanized
8 | Thickness of galvanization | mm | ≥ 80
9 | Net weight per piece | kg | 0.65-0.85
Guaranteed Technical Parameters
Dead End Hook, ABC Normal, Type I
No | Description | Unit | Required | Offered
1 | Manufacturer
2 | Country of origin
3 | Manufacturing capacity per month
4 | IEC Standard | IEC | IEC 61284
5 | Yield strength of hook | N/mm² | ≥ 400
6 | Complete dimension of hook
| a. Length | mm | 200-250
| b. Width | mm | 25-35
| c. Rod diameter | mm | 16-20
| d. Thread nominal diameter | mm | 14-18
| e. Thread minor diameter | mm | 12--16
| f. Washer outside and inside diameter | mm | As per IEC standard
| g. Washer thickness | mm | As per IEC standard
| h. Length of thread |  | 60-80
| i. Thread length | mm | 40-60
7 | Galvanization |  | Hot-dip galvanized
8 | Thickness of galvanization | mm | ≥ 80
9 | Net weight per piece | kg | 1.2-1.5
Guaranteed Technical Parameters
Dead End Hook, ABC, Type II, (for LV under MV )
No | Description | Unit | Required | Offered
1 | Manufacturer
2 | Country of origin
3 | Manufacturing capacity per month
4 | IEC Standard | IEC | IEC 61284
5 | Yield strength of hook | N/mm² | ≥ 240
6 | Complete dimension of hook
| a. Length | mm | 200-250
| b. Width | mm | 25-35
| c. Rod diameter | mm | 16
| d. Thread nominal diameter | mm | 16
| e. Thread minor diameter | mm | 14
| f. Washer outside and inside diameter | mm | As per IEC standard
| g. Washer thickness | mm | As per IEC standard
| h. Length of thread |  | 60-80
| i. Thread length | mm | 40-60
7 | Galvanization |  | Hot-dip galvanized
8 | Thickness of galvanization | mm | ≥ 80
9 | Net weight per piece | kg | 1.2-1.5
Guaranteed Technical Parameters
Dead End Tube
No | Description | Unit | Required | Offered
1 | Type designation
2 | Material |  | Aluminium Alloy
3 | Dimension ( thickness and length) | mm | 2.0*100
4 | Tensile strength | N/mm² | ≥ 240
5 | No of dead end tube per packet |  | 50
6 | Net weight per packet , g | gms | 1500
7 | Conductor crossection in mm2 | mm² | 16-185
Guaranteed Technical Parameters
Nylon Tie
No | Description | Unit | Required | Offered
1 | Manufacturer
2 | Country of origin
3 | IEC Standard | IEC | IEC 62275
4 | Material |  | Nylon
5 | Dimension ( thickness, width, length) | mm | 1.5 × 12.7 × 1030
6 | Tensile strength | N/mm² | ≥ 500
7 | No of tie wire per packet |  | 50
8 | Net weight per packet , | kg | Approx. 1.5
Guaranteed Technical Parameters
Big Collar, 40 cm
No | Description | Unit | Required | Offered
1 | - Manufacturer
2 | - Country of origin
3 | - Manufacturing capacity per month
4 | IEC Standard | IEC | IEC 61284, IEC 60383
5 | - Yield strength of Big collar (N/mm2) | N/mm² | 350
6 | - Complete dimension of Big collar
| a. Length (mm), | mm | 400
| b. Width (mm) | mm | 50
| c. Rod diameter (mm) | mm | 16
| d. Thread nominal diameter (mm) | mm | M16
| e. Thread minor diameter (mm) | mm | 14
| f. Washer outside and inside diameter (mm) | mm | AS per IEC standards
| g. Washer thickness (mm) | mm | AS per IEC standards
| h. Lead of thread | mm | 2
| i. Thread length (mm) | mm | 60
7 | -Galvanization |  | Hot-dip galvanized
8 | - Thickness of galvanization (mm) | µm | ≥ 80
9 | - Net weight per piece (kg) |  | 2.5-3.0
Guaranteed Technical Parameters
Big Collar, 30 cm
No. | Description |  | Required | Offered
- Manufacturer
- Country of origin
- Manufacturing capacity per month
| IEC Standard | IEC | IEC 61284, IEC 60383
| - Yield strength of Big collar (N/mm2) | N/mm² | 350
- Complete dimension of Big collar
| a. Length (mm) | mm | 300
| b. Width (mm) | mm | 45
| c. Rod diameter (mm) | mm | 16
| d. Thread nominal diameter (mm) | mm | M16
| e. Thread minor diameter (mm) | mm | 14
| f. Washer outside and inside diameter (mm) | mm | AS per IEC standard
| g. Washer thickness (mm) | mm | AS per IEC standard
| h. Lead of thread | mm | 2
| i. Thread length (mm) | mm | 50
| -Galvanization |  | Hot-dip galvanized
| - Thickness of galvanization (mm) |  | ≥ 80
| - Net weight per piece (kg) | kg | 2.0-2.5